GENERAL

RELATED DOCUMENTS

Related documents shall include drawings and general provisions of the Contract, including general and supplementary conditions and applicable sections of Division 1 and Division 16 specifications.

SCOPE

This Section shall include guidelines for the furnishing of all labor, equipment, materials, and performance of all operations associated with the installation of the Network  Fire Alarm and Smoke Detection System as drawn and specified herein.

The intent of drawings and specifications is to result in a complete functional networked  fire alarm and smoke detection system as described herein.

The Contractor shall provide all devices and components required to accomplish this intent whether or not specifically shown or specified.

The complete installation shall conform to the applicable sections of NFPA-72, NFPA-71, local code requirements and the National Electrical Code with particular attention to Article 760.

The work covered by this Section of the Specifications shall be coordinated with the related work as specified elsewhere under project specifications.

QUALITY ASSURANCE

Each and all components of the Fire Alarm System shall be listed as a product of a single fire alarm system manufacturer under the appropriate category by Underwriters’ Laboratories, Inc. (UL), and shall bear the “UL” Label.  All control equipment shall be listed under UL category UOJZ as a single control unit.  Partial listing shall not be acceptable.

All control equipment shall have transient protection to comply with UL 864.

Work shall be done by a qualified contractor holding a C-10 and other licenses required by authorities having jurisdiction.

Contractor shall show proof that they are an Authorized Distributor for the equipment they are installing and have been trained and certified to install and service the equipment.

Devices shall be UL listed under Standard #497B.

System control shall be UL listed for Power Limited Applications and all circuits shall be marked in accordance with NEC Article 760-23.

GENERAL SYSTEM REQUIREMENTS

System Requirements

The Fire Detection System shall be responsible for continually supervising and monitoring by zone, the following initiating, signaling and monitoring circuits designated as:

- Manual fire pull stations

- Smoke and heat detectors, including those installed under other Sections.

- Alarm signaling circuits (alarm bells, horns, speakers and visual alarms.)

The Fire Alarm System configuration for this project shall be as follows:

  - Horns shall be used for the Fire Alarm signaling.  Activation of duct smoke detectors in the Air Handling ducts shall be annunciated at the Annunciator Panel in the Main Office.  The smoke detectors and associated auxiliary relays shall be specified under this Section but will be indicated on the Drawings and installed under Sections 15850 and 15950.  Control of the air handling units through the smoke detectors and associated relays shall be carried out under Section 15950.  Extension of wiring from  the Auxiliary relays to the Fire Alarm Control Panel and annunciator shall be performed under this section.

One contractor shall furnish and install a complete Fire Alarm and Smoke Detection System as described herein and drawn

The contractor shall wired connect and make operational each and all components of the system.

The system shall include:

- Sufficient Fire Alarm Control Panels (FACPs)

- Fire Alarm System Network control equipment

- Remote Annunciators

- Manual Stations

- Automatic Fire Detectors

- Smoke Detectors

- Alarm Indicating Appliances

- Miscellaneous Components

- Wiring

- Terminations

- Raceway System

- All other necessary material for a complete operating system.

The system shall meet all national and local codes.

Fire Alarm System Supplier

The fire alarm shall be supplied by a Distributor authorized by the Fire Alarm System Manufacturer.  The supplier’s personnel shall be factory trained.

The fire alarm system supplier shall provide point to point wiring diagrams and equipment data sheets for submittal to the local authority.

System Manufacturer

The system and components shall be supplied by one manufacturer who shall have produced similar systems for a period of at least three (3) years.

The manufacturer shall be able to refer to similar installations rendering satisfactory service.

The equipment and services described in this Specification represent those supplied  and supported by Gamewell, unless noted otherwise.

System Software

The system shall be capable of self-programming upon initialization.

The system shall be capable of on-site programming to accommodate system expansion and facilitate changes in operation.

All software operations shall be stored in a nonvolatile programmable memory within the FACP.

Loss of primary and secondary power shall not erase the instructions stored in memory.

System programming shall be password protected and shall include full upload and download capability.

The system shall feature full flexibility for selective input/output control functions based on ANDing, ORing; NOTing, timing, and special coded operations shall also be incorporated in the resident software programming of the system.

Resident software shall allow for full configuration of initiating circuits. The system shall require no additional hardware to change from sensing normally open contact devices to sensing normally closed contacted devices or vice versa.  Nor shall the system require additional hardware to change from sensing normally open contact devices to sensing—and distinguishing between—a combination of current limited and non-current limited devices on the same circuit.  Nor shall the system require additional hardware for changing from a non-verification circuit to a verification circuit or vice-versa.

There shall be no limit, other than maximum system capacity, to the number of intelligent/analog devices which may be in alarm simultaneously.

The system shall have the capability of recalling alarm and trouble conditions in chronological order for the purpose of recreating an event history.

District Approval

All fire alarm, signal and control equipment shall be approved by the District in addition to other required approvals.

Certification:  Installation of the Fire Alarm System shall not be started until Drawings, including State Fire Marshall Listing numbers of all fire alarm components, are submitted to and approved by the State Fire Marshall (OSA).Written certification by the fire alarm equipment distributor or manufacturer shall be submitted to the Architect and State Fire Marshall stating that the system and its component parts are as “approved and listed” by the State Fire Marshall and that the installation conforms in all respects to the requirements set forth in Article 72, Title 24, California Administrative Code.

Alarm Operation

The actuation of any approved alarm initiating device shall automatically initiate the following operations where furnished as part of the system:

All audible alarm indicating appliances within corresponding building shall sound a fire alarm signal until the Signal Silence key is depressed.

All visible alarm indicating appliances in the corresponding building shall flash continuously until the Reset key is depressed.

The Network System Monitor shall indicate type and location of all events.

The off-site central monitoring station shall be notified automatically.

Shutdown of the corresponding HVAC system equipment shall occur until the System reset key is depressed.

Activation of all programmed outputs assigned to the initiating device shall occur until the System Reset key or the Signal Silence key is depressed.

Any subsequent zone alarm shall reactivate the alarm indicating appliances.

Alarm Indication

The alarm shall be displayed on a 160 character (4x40) LCD display on the local Fire Alarm Control Panel, and, where applicable, the remote annunciator.  The top line of 40 characters shall be the point label and the second line shall be the device type identifier.

The system alarm LED shall flash on the control panel and the remote annunciator until the alarm has been acknowledged.  Once acknowledged, this same LED shall latch on.

A subsequent alarm received from another zone shall flash the system alarm LED on the control panel and remote annunciator.  The LCD display shall indicate the new alarm information.

A pulsing alarm tone shall occur within the local building control panel, and where applicable, the remote annunciator until the event has been acknowledged.

A manual evacuation (drill) switch shall be provided to operate the alarm indicating appliances without causing other control circuits to be activated.  However, should a true alarm occur, all alarm functions would occur as described previously.

The system shall have a single key that will allow the operator to display all alarms, troubles, and supervisory service conditions including the time of each occurrence.

Any momentary opening of an initiating or indicating appliance circuit wiring shall cause an audible signal to sound at the Building Fire Alarm Panel, and where applicable, the remote annunciator for four seconds indicating a trouble condition.

Alarm Walk Test

The actuation of the “enable walk test” program at the control panel shall activate the “Walk Test” mode of the system, which shall initiate the following events:

The off-site central monitoring station connection shall be bypassed.

Control relay functions shall be bypassed.

Walk test shall be selectable by circuit.

Alarms received on normal circuits shall cause the control panel to go into alarm and override the walk test mode.

The control panel shall show a trouble condition.

The alarm activation of any initiation device shall cause the audible signals to activate for two seconds.

The panel shall automatically reset itself after signaling is complete.

The control panel shall automatically return to normal condition if there is no activity on a walk test circuit for a period of 30 minutes.

SUPERVISION

The system shall contain Class “B” independently supervised initiating device circuits.  The alarm activation of any initiation circuit shall not prevent the subsequent alarm operation of any other initiation circuit.

Each independently supervised circuit shall include a discrete LED readout to indicate disarrangement conditions per circuit.

The incoming power to the system shall be supervised so that any power failure must be audible and visually indicated at the control panel and the remote annunciator.  A green “power on” LED shall be displayed continuously while incoming power is present.

The system batteries shall be supervised so that a low battery condition or disconnection of the battery shall be audibly and visually indicated at the control panel and the remote annunciator.

The system shall have provisions for disabling and enabling all circuits individually for maintenance or testing purposes.

POWER REQUIREMENTS

Each control panel or console shall receive 120 VAC power, 60 hz., 20A  (as noted on the plans) via a dedicated circuit.

The system shall be provided with sufficient battery capacity to operate the entire system upon loss of 120 VAC power in a normal supervisory mode for a period of 24 hours with five minutes of alarm indication at the end of this period.  The system shall automatically transfer to the standby batteries upon power failure.  All battery charging and recharging operations shall be automatic.  Batteries, once discharged, shall recharge at a rate to provide a minimum of 70% capacity in 12 hours.

All circuits requiring system operating power shall be 24 VDC and shall be individually fused at the control panel.

SHOP DRAWING AND PRODUCT DATA

The system shop drawings shall include complete wiring diagrams for all components of the project.  Generic wiring diagrams, which do not apply specifically to the project, are not acceptable.  Product data sheets covering all system devices shall be furnished with shop drawings.

PRODUCTS

FIRE ALARM CONTROL PANEL

Panel Function

The Fire Alarm Control Panel shall provide power, annunciation, supervision and control for the detection and alarm system, as well as alarm signaling to alert occupants of a fire or other emergency situations.

Control panel construction shall be modular with solid state microprocessor based electronics.

Operation shall be guided via LEDs to simplify operation under any condition.

The Fire Alarm Control Panel shall be UL listed for sesitivty test of analog detectors.

Local Audible Device

A local audible device shall sound during Alarm, Trouble or Supervisory conditions.

This audible device shall sound differently during each condition to distinguish one condition from another without having to view the panel.

This audible device also shall sound during each “key-press” to provide an audible feedback to ensure that the key has been pressed properly.

Primary Controls

The following primary controls shall be visible through a front access panel:

- 160 character liquid crystal display

- Individual red system alarm LED

- Individual red pre-alarm LED

- Individual yellow supervisory service LED

- Individual yellow trouble LED

- Green “power on” LED

- Alarm Acknowledge touch switch

- Supervisory Acknowledge touch switch

- Trouble Acknowledge touch switch

- Alarm Silence touch switch

- Reset touch switch

- Manual evacuation (drill)

Interface Function

The control panel interface shall provide the following:

- Setting of time and date

- LED testing

- Alarm, trouble and abnormal condition listing

- Enabling and disabling of each monitor point separately

- Activation and deactivation of each control point separately

- Changing operator access levels

- Walk Test enable

- Running diagnostic functions

- Displaying software revision level

- Displaying historical logs

- Displaying card status

- Point listing

Point Lists Menu

For maintenance purposes the following lists shall be available from the point lists menu:

- All points list by address

- Monitor point list

- Signal/speaker list

- Auxiliary control list

- Feedback point list

- Utility point list

- LED/switch status list

Menu Lists

Scrolling through the menu options or lists shall be accomplished in a self-directing manner in which prompting messages shall direct the user.

Menu lists shall be password protected.

Acknowledgment for each abnormal condition shall be provided in accordance with NFPA 72D requirements:

Condition Display Order

The System shall display the first unacknowledged condition.

Acknowledge Password Protection

Acknowledge functions shall feature password protection if the user has insufficient privilege to acknowledge such conditions.

A message shall indicate insufficient privilege but shall allow the user to view the points without acknowledging them.

Should the user have sufficient privilege to acknowledge, a message will be displayed informing the user that the condition has been acknowledged.

Acknowledgement

After all points have been acknowledged, the LEDs shall glow without blinking and the audible signal shall be silenced.

The total number of alarms supervisory and trouble conditions shall be displayed along with a prompt to review each list chronologically.  The end of the list shall be clearly defined.

Alarm Silencing:

When the “Alarm Silence” button is pressed all alarm signals shall cease operation, except during alarm silence inhibit mode.

It shall be possible to selectively program signal circuits as non-silenceable.

System Reset:

The system reset button shall be used to return the system to its normal state after an alarm condition has been remedied.

The LCD display shall step the user through the reset process with simple English Language messages including a final message indicating the system has been returned to the normal condition.

Function Keys:

Additional function touch switches shall be provided to access status data for the following points:

- Initiating device circuits

- Indicating appliance circuits

- Auxiliary relays

- Feedback points

- All other input/output points

Available Status Data

The following status data shall be available.

- Primary State of point

- Zone, Point Address and Card type information

- Circuit Status

- Current priority of outputs

- Disable/Enable status

- Automatic/Manual Control Status of output points (Hand-Off/Auto Switches)

- Relay Status

Utility Points:

Each control panel shall have dedicated utility point supervisory and acknowledge buttons. Activation of a utility point shall activate the system supervisory service audible signal and illuminate the appropriate utility point LED on the control panel, at the Master Control Console and at the guard shack network control panel.

Pressing the appropriate acknowledge button shall silence the audible alarm, while maintaining the LED ‘ON’ indicating the OFF-normal condition.

Restoring the condition to its normal position, or locally resetting the acknowledge switch shall extinguish the LED, indicating normal conditions.

Alarm History Log:

The system shall be capable of logging and storing up to 1000 events in the History Log.  These events shall be stored in a battery protected random access memory.  Each recorded event shall  include the time and date of that event’s occurrence.

The following Alarm History events shall be stored:

- Alarms

- Alarm Acknowledgment

- Alarm Silence

- System Reset

- Alarm Historical log cleared

Trouble History Log

The following Trouble History events shall be stored:

- Trouble conditions

- Supervisory alarms

- Trouble acknowledgment

- Supervisory acknowledgment

- Walk Test results

- Trouble Historical log cleared

Access Levels

There shall be four (4) access levels with level 4 being the most secure level.

Level 1 actions shall not require a passcode.

Passcodes shall be numerical and shall consist of up to six (6) digits. Changes to passcodes shall be made only by authorized personnel.

Printer/CRT Interface Card:

The control panel shall include an output port (RS-232) capable of operating remote CRT’s and/or printers from a  Central Processing Unit.

Remote Station Interface:

A digital alarm communicator transmitter, remote station transmitter, or municipal tie shall provide interface with a remote control station for monitoring alarm and trouble conditions.  Communication to central station shall be by way of two supervised telephone lines.

Addressable Interface Module:

The system must provide communication with initiating and control devices individually.  All of these devices will be individually annunciated at the control panel.  Annunciation shall include the following conditions for each point:

- Alarm

- Trouble

- Open

- Short

- Device missing/failed

2.1.20.2    Allow for a minimum of 4 Analog Addressable loops.

All Addressable Devices

All addressable devices shall have the capability of being disabled or enabled individually.

Up to 126 addressable devices may be multi-dropped from a single pair of wires.  Systems that require factory reprogramming to add or delete devices are unacceptable.

The communication format must allow t-tapping of the circuit wiring.

Alarm Signaling:

The Fire Alarm Control Panel shall provide sufficient power and signal circuit capability to meet the requirements of the plans and specifications and to comply with ADA (Americans with Disabilities Act) requirements.

The Fire Alarm Control Panel and Power Supplies shall be designed to accommodate all  signaling circuits and 20% spare capacity.

The Fire Alarm Control Panel shall allow for field programming operation of the signal circuits  (i.e. march time, zone coded, zone-signal linking, etc.)  This capability shall be included in the  system firmware with no additional cost to the Owner.

Cabinets and Consoles:

The Fire Alarm Control Panel and annunciator cabinets shall be sized to accommodate all components and modules specified and required for a complete system.

- Additional space for future expansion shall be provided in the cabinet .

- Cabinets shall be capable of surface or flush mounting as indicated.

- Sheet steel cabinets shall be completely primed and finish painted.

- The Control Consoles shall accommodate, in one section, power supply, modules and components required for fire alarm control, and system network control and annunciator.

All Fire Alarm Control Panels shall be Gamewell IdentiFlex 610 or approved equal. (CSFM 7165-1288:154)

Annunciator Panel

The Fire Alarm Control Panel shall provide an LCD annunciator where drawings indicate remote area annunciation of the corresponding fire alarm signals.

The annunciator shall indicate Alarm, Supervisory and Trouble conditions by dedicated LED’s and an audible signal.

The annunciator shall feature an acknowledge button which, when depressed, shall silence the audible signal.

A 160-character LCD display shall provide the same message as displayed on the corresponding Fire Alarm Control Panel.  The annunciator panel shall be capable of alarm silence and system reset functions.

The annunciator shall be panel mounted with controls visible through a front access panel and operable only by activating an enable key switch.

The annunciator panel shall be Gamewell RAN2 or approved equal. (CSFM 7120-1288:149)

ALARM INITIATING DEVICES

Addressable/Analog Detectors:

All Addressable/Analog Detectors shall not be polarity sensitive on the SLC loop wiring. Polarity sensitive devices will not be acceptable.

All addressable/analog smoke and heat detectors as specified below shall be twist lock mounted into their bases.

The detector unit shall contain electronics that communicate the detector chamber analog value to determine (normal, alarm, trouble) to the control panel over two wires.  The same two wires shall also provide power.

Upon removal of the head, the base shall transmit a trouble signal to the control panel.

It shall be possible to change out detector heads without having to reprogram or address the unit.

The detector's address shall be stored in the base.  Detectors that store address information in the head shall not be allowed.

Addressable/analog detectors shall be U.L. listed.

Photoelectric Type Detectors:

Addressable/analog photoelectric smoke detectors shall sense the presence of smoke particles between a light source and a receiver within the detector.

Sensitivity shall be set by the manufacturer and provisions shall be included to check the sensitivity at the control panel without generating smoke.

The unit shall be equipped with a visible LED for alarm indication.

The detector screen and cover shall be easily removable for field cleaning.

Addressable/analog photoelectric detectors shall be Gamewell Model XP95-P or approved equal. (CSFM 7272-1394:104)

Conventional Photoelectric Detectors:

The conventional photoelectric smoke detector shall sense the presence of smoke particles between a light source and a receiver within the detector.

Sensitivity shall be set by the manufacturer.

The detector shall contain an integral LED that shall latch in when the unit goes into alarm.

The detector screen and cover shall be easily removed for field cleaning.

The Conventional photoelectric detector shall be Gamewell Series 60 Model 71033 or approved equal. (CSFM 7272-1394:100)

Duct Detectors

Addressable/analog duct type smoke detectors shall operate on photoelectric principal, as indicated and previously specified.

For mounting on ductwork the detector shall include a sampling tube which shall be field cut to size to cover complete duct width.

The unit shall be restorable.

The detector shall be capable of stable operation under varying conditions, including vibration, mechanical shock and changes in supply voltage, ambient temperature and barometric pressure.

Unit shall be capable of interfacing with either an internal relay or a remote relay module as required for fan shutdown, and auxiliary contacts for Building Automation System interface.

The unit shall be equipped with a visible LED for alarm indication.

The detector screen and cover shall be easily removable for field cleaning.

Addressable duct detectors shall be Gamewell Model No. XP95-PD photoelectric detectors specified above, or approved equal. (CSFM 3240-1004:100)

2.2.1.5. Addressable Heat Detectors:

        - Addressable/analog heat detector shall operate as indicated and previously specified.

        - The Alarm Temperature shall be programmable from 134* F to 194* F in 1 Celcius incraments.

        - Heat Detector shall be programmable for Rate of Rise On/Off.

        - The Heat Detector shall be capable of operating in an ambient temperature range of 32* to 154*F.

        - The Heat Detector shall monitor temperature by using a single thermister network which provides a voltage output propotional to the external air Temperature.

        - The Heat Detector shall be a Gamewell XP95-T or approved equal.  (CSFM 7270-1394:105)

2.2.1.6 Conventional Heat Detectors:

2.2.1.6.1.   Conventional Thermal Heat detector shall operate as indicated and previously specified.

        - The fixed temperature rating  shall be  135* F, 160*F or210* F.

        - Heat Detector shall be Rate of Rise.

        - The Heat Detector shall be a Gamewell Series 60 71035 or approved equal.  (CSFM 7270-1394:102)

2.21.7 Multi-Sensor:

2.2.1.7.1   The	Multi-Sensor includes both Photoelectric and Thermal sensing elements integrated into one unit.

        - The Sensor shall be capable of digitally transmitting not only its address to the FACP, but also the combined data consisting of an analog value from the photoelectric chamber and the thermal element for analysis.

        - Sensor head utilizes common analog address style bases.

        - Address is set by Xpert Addressing Cards and is stored in the sensor base.

        - Alarm and Trouble conditions are determined by the microprocessor in the head, which also automaticlly performs drift compensation.

        - The Multi-Sensor shall be a Gamewell XP95-M or approved equal.

Addressable Manual Stations:

The addressable manual station shall be capable of field programming of its “address” location on an addressable initiating circuit.

The manual station shall be fitted with screw terminals for field wire attachment.

The manual station shall be non-coded, semi-recessed, and restorable.

The manual station shall be lift type, double action with no delay feature and shall be capable of having break-glass rod as standard feature but shall not depend upon the glass rod to hold the station in normal position.

The addressable manual station shall be U.L. listed.

The addressable manual station shall be Gamewell Model No. MS-95 or approved equal. (CSFM 7150-1288:148)

Conventional Manual Station:

The manual station shall be fitted with screw terminals for field wire attachment.

The manual station shall be non-coded, semi-recessed, and restorable.

The manual station shall be lift type, double action with no delay feature and shall be capable of having break-glass rod as standard feature but shall not depend upon the glass rod to hold the station in normal position.

The manual station shall be U.L. listed.

The manual station shall be Gamewell Model No. M46-28 or approved equal. (CSFM 7150-1288:108)

Point Identification Device (PID):

A Point Identification Device (PID) shall be suitable for monitoring a single conventional initiating device type such as waterflow, manual station or non-addressable detectors, and for control of evacuation indicating appliances and AHU systems.  Modules shall include cover for surface mounting. The PID shall provide for feedback to the FACP for positive confirmation of the controlled devices activity.

A Point Identification Device shall be provided for interfacing normally open direct contact devices to any of the addressable initiating circuits, and providing HVAC equipment shutdown.  Control module relay contacts are rated 2A @ 120VAC or 28VDC, resistive.

A Point Identification Device shall be Gamewell Model No. PID-95 for single point applications and devices. (CSFM 7300-1288:147)

Collective Zone Interface Module (CZI):

A Collective Zone Interface Module (CZI) shall be suitable to connect supervised conventional initiating device or zone of initiating such as waterflow switches, tamper switches, detectors and other such devices to any of the intelligent analog loops.

The Collective Zone Interface Module shall be provided for configuring remotely located conventional zones on the analog circuit. The Collective Zone Interface shall provide power for up to 25 conventional type detectors. The Collective Zone Inteface are designed for surface or flush mounting and are provided with an LED for annunciation. The CZI shall utilize a 4 11/16” by 3” deep backbox and shall include a cover for surface mounting.

The Collective Zone Interface Module shall be Gamewell Model No. CZI-95.  (CSFM 7300-1288:147)

Control Elements

A Remote Control Element (RCE), Building Control Element (BCE) and Signal Control Element (SCE) shall be provided for any devices that require control, activation or feedback during Fire Alarm condition such as stairwell pressurization fans, smoke exhaust, and damper control. Provide Gamewell Model No. RCE-95 Control Element with one Form C relay Rated @2 amps @ 30VDC suitable for flush or surface mounting, SCE-95 for activation of remote signal circuits, and BCE-95 for fan control. The Control Elements shall be Gamewell Model No. RCE-95, SCE-95, BCE-95. (CSFM 7300-1288:147)

ALARM INDICATING DEVICES

Visual Alarm Signals:

Visual signals shall be suitable for flush or surface mounting and shall be provided for all locations as shown on the plans.

Visual alarm signals candella ratings shall be per NFPA-72 Chapter 6.

Provide a protective cover for devices in the Gymnasium area.

Visual Signals shall be Gamewell RSS Series 72035 or approved equal.

(CSFM 7125-0785:141)

Weather Proof Horn Signals:

Horn shall be capable of being flush or surface mounted.

Horn shall be mounted in an approved weather proof box..

Horn shall be Gamewell AH-WP Series 71711 or approved equal. (CSFM 7125-0785:131)

Horn Strobe Signals:

Horn Strobes shall be capable of being flush or surface mounted.

Strobel candella ratings shall be per NFPA 72 Chapter 6.

Units shall be installed where indicated on the plans.

Horns Strobes shall be Gamewell AS Series 72032 or approved equal.(CSFM 7125-0785:131)

Remote NAC Expander/power supply:

The Fire Alarm System shall be designed with remotely located Notification Appliance Circuit expander/power supplies for the support of notification appliances.

The remote power supplies shall be fully supervised and shall provide a minimum of four 2 Amp NAC’s (up to 8 Amps).

The Remote Power supply shall be capable of supplying the Sync Protocoll for Signals.

The Remote Power Supply shall be capable of providing 1.5 amp of Aux Power without taking away one of the 4 NAC Circuits.

The NAC Expander/Power /Supply shall be an Gamewell FireForce 8.  (CSFM 7315-1288:162))

Fire Alarm System Network

The Fire Alarm System Network shall consist of all necessary hardware and software equipment to perform the fire alarm and detection operations.

Nodes (FACPs) as defined for this specification shall be intelligent, microprocessor based devices that connect to, and handle network communications in a Broadcast Message format using a Master Slave configuration.  Control by Event programs for each nodes in the system being able to respond to Broadcast Messages shall be distributed among the nodes.

By porgrammable selections at each node:

The specific detail information of any point connected to any node in the network may be accessable to the network

Any point information may be incorporated into the custom control program of any node and operated upon as though that point was physically connected to that node.

Points within each node shall be able to be grouped by area, type of device, type of function, or any other user selectable category, and custom labeled as a group.  A group shall be acted upon as though it was a point for the purpose of interaction with the node custom control by event program.

FIRE ALARM SYSTEM NETWORK GENERAL REQUIREMENTS

Furnish and install all network fire alarm system equipment as defined by these specifications, to be wired, connected, and left in first class operating condition.

Network operations shall be via  communication links that connect all network nodes and include data transfer.  All communications wiring shall be electrically supervised.

The network shall operate using a full duplex, RS-422 communication technique at a data rate of 9600 baud. The Node to Node communication shall be on 2 pair Shielded twisted cable or Fiber network.

To insure compatibility with growth and future expansion of  the Fire Alarm System the proposed network shall have a capacity of 250 nodes.  Networks that do not provide a minimum of 250 nodes are unacceptable.

Fire Alarm Netowrk OperatioN

    - Network operation for anu manual or automatic fire alarm initiaing device activation shall be as follows:

      - The node connected to the alarmed device shall operate in accordance with its programmed response.

      - The change in status shall be reproted to the Network Master.  It shall be updated with the alarm condition to include:

        - Public point node identification and point location.

        - Non-Public point node identification and point location.

        - The red ALARM LED shall flash on the monitoring node, and aon all connected network nodes programmed to recognize that alarm, until the alarm has been manually acknowledged.  When the alarm has been acknowldged, this same LED shall latch on.  A subsequent alarm received after any acknowledgement shall again flash the same LED’s.

        - The source of alarm shall annunciate via English language description on the alphanumeric display at the monitoing node and all other nodes programmed to respond to that alarm.

        - All nodes shall respond to the alarm information in accordance with their individually programmed response which may include operation of control functions both connected to that node and on other nodes if public.

        - Input from any panel node may automatically activate an output at any or all other panel nodes on the network.

        - All alarm conditions shall be visually indicated at the Master Node and at all remote annunciators as programmed.

        - All alarms hsall be recorded with the time and date on the designated network printer.

        - The Network operation shall be such that the alarm operation of any alarm-initiating device shall not prevent the subsequent alarm operation of any other initiating device due to wiring or power limitations.

      - Time Keeping

        - Network time synchronization with seconds resolution accuracy shall be provided by the Master Control Panel.  During periods without any time or date changes, the network shall maintain time synchronization by network communication once every 24 hours.  In the event that the network time keeping  functio is unavailable, each node shall maintain its own local time and date reference using an internal clock controled by its CPU card.

      - Emergency Operation

        - In the event of failure of the Node CPU or loss of total communication the the Network Master Control the following sequence shall take place.

          - Loss of the Node CPU or loss of communication shall be annunciated on the network Master Display.

          - Remote Annunciators shall indicate loss of communication.

          - A Trouble shall be transmitted to the monitoring station.

Digital Alarm Communicator Transmitter:

The 4 Channel Slave Fire Communicator shall be digital type, UL listed for fire reporting to a central station.

Panel shall provide automatic battery back-up power.

The control and communicator shall have the capability to supervise two telephone lines, seize the phone line and send the alarm signal on one or both lines without the addition of any more equipment.

The alarm signal shall indicate all addressable alarm and trouble events.  Restoration from alarm or trouble shall also be tranmitted.

The Digital Fire Communicator shall be Gamewell COM4-C or equal.  (CSFM 7300-0559:120)

Printer

Printers shall be provided and installed as shown.

All printed information shall include time and date.

A desktop 80 column printer shall provide a hard copy record of system events.  The printer shall support the following features:

- 120 VAC input power

- 180 characters per second

- kilobytes buffer capacity

- Impact dot matrix

- Cartridge type ribbon

- Friction feed for cut forms

- Tractor feed for continuous 9-1/2” wide pin-to-pin fanfold paper

- UL listed

2.5.4    The Printer shall be a Gamewell SN600-PTR or approved equal.  (CSFM 7300-1288:151)

EXECUTION

INSTALLATION

The contractor shall provide and install the system in accordance with the plans and specifications, all applicable codes and the manufacturer’s recommendations.

The Fire Alarm panel my be located with the telephone equipment.  Annunciators must be visable in the Administration Office.

The Voice Evacuation Panel shall be located in the Gynasium.

Detector Installation

Detector locations shall be no closer than 4’ from air supply outlets, nor in beam pockets deeper than 12”.  No detector shall be purposely recessed in a ceiling.

Duct type smoke detectors shall be provided under this section of the specification for mounting by the mechanical contractor.  All conduit, wire and final connections shall be performed by the Division 16 contractor.

Programming

The Contractor shall perform all programming of system including local panel programming and network programming.

The Contractor shall perform the necessary assigning of system points.

Wiring

The contractor shall furnish and install in accordance with manufacturer’s instruction all wiring, conduit, and outlet boxes for installation of a complete system as described herein and drawn.

Wiring for the fire alarm system , in general, shall consist of a minimum of: #18 2 conductor FPL type conductors for data loop initiating circuits. A minimum of  #20 2 conductor shielded for the Serial Data Communication Circuits. A minimum of #14 THHN/THWN type conductors for indicating NAC circuits.

All wiring shall meet NEC 760 for fire alarm system wiring.  All wiring shall be tagged at junction points and shall test free of grounds and shorted between conductors.  All additional labor costs incurred by the Fire Alarm System Technician to clear wiring faults shall be charged to the installing contractor.

All final terminations of the field wiring shall be made by or under the direct supervision of the Fire Alarm System Manufacturer’s representative.  Any damage to the panel as a result of the contractor terminating wires or powering up the panel without the supervision of an authorized representative of the Fire Alarm Panel Manufacturer shall be charged to the installing contractor.

Miscellaneous

All junction boxes shall be painted red and labeled “Fire Alarm.”  Color coded wiring shall be maintained throughout the installation.

Installation of equipment and devices relevant to other work in the contract shall be closely coordinated with the appropriate subcontractors.

The Contractor shall clean all dirt and debris from the interior and exterior of the fire alarm equipment after completion of the installation.

The manufacturer’s Authorized Representative shall provide on-site supervision of installation.

ON-SITE START-UP

System Check

Prior to energizing any part of this system, the factory authorized representative shall check thoroughly the installation, and perform pre-start checks.  This representative shall check all points, fire alarm panels and complete network to ensure proper operation, and make any needed repairs and/or replacements required.  Sufficient time shall be included in the project bid to cover all required start-up assistance and  testing.

Testing

The Contractor shall test fully the completed fire alarm system in accordance with NFPA-72H in the presence of the Owner’s Representative and under the direction of the factory authorized representative.

Testing shall be provided as required by the local Fire Marshal.

Upon successful completion of tests, the Contractor shall so certify in writing to the Owner’s Representative.

Alarm horn sound levels shall be tested during Owner’s normal operating conditions to ensure emergency signaling is of an approved sound level over normal ambient noise. The test shall be performed during a 90-day period following the above “Fire Marshal” test on a date to be selected by the Owner.

TRAINING

Demonstration

A factory authorized representative shall demonstrate the the fire alarm system.

The demostration shall simulate possible operating conditions and alarms.

Scope of Training

Training shall include documentation and hands-on exercise necessary to enable the Owner’s Representative to assume full programming and operating responsibility.

Project Bid

Contractor shall include the costs of schooling for sending two District employees to the factory to become Certified for Maintenance on the Fire Alarm Panel, software and accessories. The District will provde transportation lodging and meals during for the training.

The project bid shall include sufficient time for required initial training and follow-up assistance for the school personnel.

Technical Support

Technical support and service by factory trained personnel shall be available from the manufacturer’s representative.

central station

The system shall be connected to an approved off-site central monitoring station with equipment and installation methods as required and approved by local fire department.

A three (3) year renewable contract with the central station shall be included beginning the day the system is successfully tested and completed.

The cost of the Central Station tie shall be broken out separately from the fire alarm system bid.

WARRANTY

The Installing contractor shall warranty all wiring to be free from inherent mechanical and electrical defects for a period of one year from installation.

The Manufacturer’s Representative shall provide the Owner’s Representative and Certification of Installation for the entire system certifying that the system was installed and is operating properly and in accordance with these specifications.

The Installing Contractor shall provide the Owner with a three (3) year Maintenance Proposal upon completion of the Project.