ENGINEERING SPECIFICATION

IPGSM-4G COMMUNICATOR

PART 1.0 - GENERAL

1.1. DESCRIPTION:

A. This section of the specification includes the furnishing, installation, connection and

testing of the IPGSM-4G Communicator.

B. The IPGSM-4G Communicator shall comply with requirements of NFPA

Standard No. 72 except as modified and supplemented by this specification.

C. The IPGSM-4G Communicator shall be manufactured by an ISO 9001 certified

company and meet the requirements of BS EN9001: ANSI/ASQC Q9001-1994.

D. The IPGSM-4G Communicator shall be manufactured or supplied 100% by a

single U.S. manufacturer (or division thereof).

E. Underwriters Laboratories Inc. (UL) – USA

F. The installing company shall employ NICET (minimum Level II Fire Alarm

Technology) technicians on site to guide the final check-out and to ensure the systems

integrity.

G. The IPGSM-4G Communicator shall meet requirements of UL ANSI 864 Ninth

Edition

1.2. SCOPE:

- IPGSM-4G Communicator shall be installed in accordance to the project

specifications and drawings.

B. Basic Performance:

1. The IPGSM-4G Communicator connect directly to the primary and secondary

analog UL Listed Fire Alarm Control Panel telephone ports.

2. The Communicator will communicate to GSM networks in the area including 2G,

3G and 4G. The multi-GSM platform technology automatically detects and

chooses the best network in the area based on signal strength and immediately self

adjusts for operation.

3. Supports both dynamic (DHCP) or Public and Private Static IP addressing.

4. Communicates over any type of customer-provided Ethernet 10/100 Base network

connection (LAN or WAN), DSL modem or cable modem.

5.  Data transmits over standard contact-ID protocol is secured with the industry’s

advanced encryption standard (AES 256 bit).

6.  Dual path communications: Uses Internet or GSM as primary.

- User programmable: 7720P Programming Tool

8.   Diagnostic LEDs: Signal strength and status indications.

9.   IP and GSM tested everyday

10.  All circuits shall be power-limited, per UL864 requirements.

C. BASIC SYSTEM FUNCTIONAL OPERATION

When a fire alarm condition (Alarm, Supervisory or Trouble) is detected, the Fire

Alarm Control Panel goes off-hook to dial the central station. The IPGSM-4G Dialer

Capture Module detects the off-hook condition and provides the fire panel with a dial

tone. When the fire panel detects the dial tone, it begins dialing the central station.

The Dialer Capture Module considers the three second period after dialing as the

number dialing has been completed. After the dialing is completed, the Dialer

Capture Module returns a handshake to the fire panel.

The fire panel then sends the contact ID reports to the Dialer Capture Module, which

in turn sends a kiss-off after the report is successfully received from the fire panel.

The Dialer Capture Module sends the contact ID reports to the  iGSM

communications module. When all the reports are sent, the fire panel goes on-

hook. The iGSM communications module then transmits the messages to the central

station (either over the internet or the GSM network).

1.3. SUBMITTALS

A. General:

1. Two copies of all submittals shall be submitted to the Architect/Engineer for

review.

2. All references to manufacturer's model numbers and other pertinent information

herein is intended to establish minimum standards of performance, function and

quality. Equivalent compatible UL-listed equipment from other manufacturers

may be substituted for the specified equipment as long as the minimum standards

are met.

3. For equipment other than that specified, the contractor shall supply proof that

such substitute equipment equals or exceeds the features, functions, performance,

and quality of the specified equipment.

B. Shop Drawings:

1. Sufficient information, clearly presented, shall be included to determine

compliance with drawings and specifications.

2. Include manufacturer's name(s), model numbers, ratings, power requirements,

equipment layout, complete wiring diagrams and conduit layouts.

C. Manuals:

1. Submit simultaneously with the shop drawings, complete operating and

maintenance manuals listing the manufacturer's name(s), including technical data

sheet(s).

- Wiring diagrams shall indicate internal wiring for IPGSM-4G Communicator

and the interconnections between the items of equipment.

3. Provide a clear and concise description of operation that gives, in detail, the

information required to properly operate the equipment and system.

1.4. GUARANTY:

All work performed and all material and equipment furnished under this contract shall

be free from defects and shall remain so for a period of at least one (1) year from the

date of acceptance. The full cost of maintenance, labor and materials required to

correct any defect during this one year period shall be included in the submittal bid.

1.5. MAINTENANCE:

A. Maintenance and testing shall be on a semi-annual schedule or as required by the

local AHJ. A preventive maintenance schedule shall be provided by the contractor

describing the protocol for preventive maintenance.

B. As part of the bid/proposal, include a quote for a maintenance contract to provide

all maintenance, tests, and repairs described below. Include also a quote for

unscheduled maintenance/repairs, including hourly rates for technicians trained on

this equipment and response travel costs for each year of the maintenance period.

Submittals that do not identify all post contract maintenance costs will not be

accepted. Rates and costs shall be valid for the period of five (5) years after

expiration of the guaranty.

1.6. POST CONTRACT EXPANSIONS:

A. The contractor shall have the ability to provide parts and labor to expand the

system specified, if so requested, for a period of five (5) years from the date of

acceptance.

B. Submittals that do not include this estimate of post contract expansion cost will not

be accepted.

1.7. APPLICABLE STANDARDS AND SPECIFICATIONS:

The specifications and standards listed below form a part of this specification. The

system shall fully comply with the latest issue of these standards, if applicable.

A. National Fire Protection Association (NFPA) - USA:

No. 13	Sprinkler Systems

No. 70	National Electric Code (NEC)

No. 72	National Fire Alarm Code

No. 101 Life Safety Code

No. 38	Manually Actuated Signaling Boxes

No. 217 Smoke Detectors, Single and Multiple Station

No. 228 Door Closers–Holders for Fire Protective Signaling Systems

No. 268 Smoke Detectors for Fire Protective Signaling Systems

No. 268A Smoke Detectors for Duct Applications

No. 346 Waterflow Indicators for Fire Protective Signaling Systems

No. 464 Audible Signaling Appliances

No. 521 Heat Detectors for Fire Protective Signaling Systems

No. 864 Control Units for Fire Protective Signaling Systems

No. 1481 Power Supplies for Fire Protective Signaling Systems

No. 1610 Central Station Burglar Alarm Units

No. 1638 Visual Signaling Appliances

No. 1971 Visual Signaling Appliances

No. 2017    General-Purpose Signaling Devices and Systems

- The IPGSM-4G Communicator shall be ANSI 864, 9th Edition Listed.

B. The system and its components shall be Underwriters Laboratories, Inc. listed

under the appropriate UL testing standard as listed herein for fire alarm

applications and the installation shall be in compliance with the UL listing.

C. Local and State Building Codes.

D. All requirements of the Authority Having Jurisdiction (AHJ).

1.8. APPROVALS:

A. The system shall have proper listing and/or approval from the following nationally

recognized agencies:

UL	      Underwriters Laboratories Inc

CSFM	      California State Fire Marshal

PART 2.0 PRODUCTS

2.1. EQUIPMENT AND MATERIAL, GENERAL:

A. All equipment and components shall be new, and the manufacturer's current model.

The materials, appliances, equipment and devices shall be tested and listed by a

nationally recognized approvals agency for use as part of a fire protective signaling

system, meeting the National Fire Alarm Code.

B. All equipment and components shall be installed in strict compliance with

manufacturers' recommendations. Consult the manufacturer's installation manuals

for all wiring diagrams, schematics, physical equipment sizes, etc., before

beginning system installation.

C. All equipment must be available "over the counter" through the Security

Equipment Distributor (SED) market and can be installed by dealerships

independent of the manufacturer.

2.2. CONDUIT AND WIRE:

A. Conduit:

1. Conduit shall be in accordance with The National Electrical Code (NEC), local

and state requirements.

2. Where required, all wiring shall be installed in conduit or raceway.  Conduit fill

shall not exceed 40 percent of interior cross sectional area where three or more

cables are contained within a single conduit.

3. Cable must be separated from any open conductors of power, or Class 1 circuits,

and shall not be placed in any conduit, junction box or raceway containing these

conductors, per NEC.

4. Conduit shall not enter the fire alarm control panel, or any other remotely

mounted control panel equipment or backboxes, except where conduit entry is

specified by the Fire Alarm Control Panel manufacturer.

- Conduit shall be 3/4 inch (19.1 mm) minimum.

B. Wire:

1. All IPGSM-4G Communicator wiring shall be new.

2. Wiring shall be in accordance with local, state and national codes (e.g., NEC

Article 760) and as recommended by the manufacturer of the IPGSM-4G

Communicator.

3. All wire and cable shall be listed and/or approved by a recognized testing agency

for use with a protective signaling system.

4. Wire and cable not installed in conduit shall have a fire resistance rating suitable

for the installation as indicated in NEC 760 (e.g., FPLR).

5. All field wiring (with exception of external communications Ethernet) shall be

electrically supervised for open circuit and ground fault.

C. Terminal Boxes, Junction Boxes and Cabinets:

All boxes and cabinets shall be UL listed for their use and purpose.

2.3. IPGSM-4G COMMUNICATOR:

- The Communicator shall be a Fire-Lite Alarms Model IPGSM-4G. Central station supervisory equipment shall be a Honeywell’s

AlarmNet Network Control Center listed to UL-864 standards.

- IPGSM-4G Communicator is connected to any Fire Alarm Control Panel DACT telephone ports, the system shall be capable of transmitting Contact ID formatted alarms, supervisory or troubles to a Honeywell’s AlarmNet Network Control Center equipped with a Honeywell AlarmNet receiver via Ethernet over a private or public WAN/LAN, Intranet or Ethernet.

C. System Capacity and General Operation

- The IPGSM-4G Communicator shall include connections to the Fire Alarm Control     Panel’s phone outputs and shall convert the contact ID protocol into Ethernet

Packets.

2.   The IPGSM-4G Communicator shall be completely field-programmable locally

from a 7720P Programming Tool.

3.   The IPGSM-4G Communicator shall be capable of transmitting events in contact

ID format.

4.   Communication shall include vital system status such as:

-	Independent Zone (Alarm, trouble, non-alarm, supervisory)

-	Independent Addressable Device Status

-	AC (Mains) Power Loss

-	Low Battery and Earth Fault

-	System Off Normal

-	24 Hour Test Signal

-	Abnormal Test Signal (per UL requirements)

- The IPGSM-4G Communicator shall support independent zone reporting

via the Contact ID format. This format shall enable the central station to have  details concerning the location of the fire for emergency response.  The IPGSM-4G Communicator shall be capable of providing simulated phone lines to the Fire Alarm Control Panel. The IPGSM-4G Communicator shall communicate over IP or GSM primary and shall be transparent to the Fire Alarm Control Panel normal operation over phone lines.

6. The supervising station shall consist of a Honeywell’s AlarmNet Network

Control Center receiver.

D. Enclosures:

- The IPGSM-4G Communicator shall be housed in a UL-listed cabinet.

- The back box and door shall be constructed of steel with provisions for

electrical conduit connections into the sides and top.

E. Power Supply:

- The main power supply shall operate on 120 VAC, 60 Hz, 0.50Amp and shall

provide all necessary power for the IPGSM-4G Communicator.

2. Positive-Temperature-Coefficient (PTC) thermistors, circuit breakers, or other

over-current protection shall be provided on all power outputs. The power

supply shall provide an integral battery charger. Battery arrangement may be

configured in the field.

3. The main power supply shall continuously monitor all field wires for earth

ground conditions.

1.11. BATTERIES:

- Upon loss of Primary (AC) power to the IPGSM-4G Communicator, the battery

shall have sufficient capacity to power the IPGSM-4G Communicator for required

standby time (24 hours) followed by 5 minutes of alarm.

B. The battery is to be completely maintenance free. No liquids are required. Fluid

level checks for refilling, spills, and leakage shall not be required.

PART 3.0 - EXECUTION

3.1. INSTALLATION:

A. Installation shall be in accordance with the NEC, NFPA 72, local and state codes,

as shown on the drawings, and as recommended by the major equipment

manufacturer.

B. All conduit, junction boxes, conduit supports and hangers shall be concealed in

finished areas and may be exposed in unfinished areas.

3.2. TEST:

The service of a competent, NICET level II technician shall be provided to technically supervise and participate during all of the adjustments and tests for the system. All testing shall be in accordance with NFPA 72.

A. Before energizing the cables and wires, check for correct connections and test for

short circuits, ground faults, continuity, and insulation.

3.3. FINAL INSPECTION:

A. At the final inspection, a minimum NICET Level II technician shall demonstrate

that the system functions properly in every respect.

3.4. INSTRUCTION:

A. Instruction shall be provided as required for operating the system. Hands-on

demonstrations of the operation of all system components and the entire system

including program changes and functions shall be provided.

B. The contractor or installing dealer shall provide a manual indicating

"Sequence of Operation."