Architects and Engineering Specification

System Sensor L-Series Low Frequency 520 Hz sounder Strobe

The 520 Hz sounder strobe shall be a System Sensor L-Series Model _______ listed to UL 1971 and UL 464 and shall be approved for fire protective service. The 520 Hz sounder strobe shall be wired as a primary signaling notification appliance and comply with the Americans with Disabilities Act requirements for visible signaling appliances, flashing at 1 Hz over the strobe’s entire operating voltage range. The strobe shall have field-selectable candela settings including 15, 30, 75, 95, 110, 135, 185 for wall mounted units and 15, 30, 75, 95, 115, 150, 177 for ceiling mounted units.  The strobe light shall consist of a xenon flash tube and associated lens/reflector system. The 520 Hz sounder shall have two audibility options and an option to switch between a temporal three, temporal four pattern and a non-temporal (continuous) pattern. These options are set by a multiple position switch. The 520 Hz sounder on 520 Hz sounder strobe models shall operate on a coded or non-coded power supply.  Indoor L-Series products shall operate between 32 and 120 degrees Fahrenheit from a 24V regulated DC or full-wave rectified unfiltered power supply.

The 520 Hz sounder strobe shall mount to a standard 4 × 4 × 1½ -inch back box, 4-inch octagon back box, double gang back box, or a single-gang 2 × 4 × 17⁄8-inch back box. Each appliance ships with a mounting plate for its specific size.  The notification appliance circuit wiring shall terminate at the mounting plate.

The L-Series 520 Hz sounder strobe and the Sync•Circuit™ Module MDL3 accessory, if used, shall be powered from a non-coded notification appliance circuit output and shall operate on a nominal 24 volts. The Sync•Circuit Module MDL3 operating at 24-volt-rated notification appliance circuit outputs shall operate between 16.5 and 33 volts.  If the notification appliances are not UL 9th edition listed with the corresponding panel or power supply being used, then refer to the compatibility listing of the panel to determine maximum devices on a circuit.  Appliances will not sync when in the Temp four setting.

The 520 Hz sounder strobe shall be plug-in and shall have the ability to check wiring continuity via a shorting spring on the universal mounting plate. The shorting spring shall also provide tamper resistance via an open circuit if the device is removed.

All notification appliances shall be backward compatible.