HONEYWELL FARENHYT SERIES IFP-300ECS ( 254 POINT)  FIRE ALARM

WITH EMERGENCY COMMUNICATION SYSTEM USING HOCHIKI PROTOCOL

ENGINEER/ARCHITECT SPECIFICATION

# Version 1.0

5/17

Honeywell

1985 Douglas Drive

Golden Valley, MN 55422

Tel: 1-800-328-0103

http:\\www.farenhyt.com

SECTION ONE: GENERAL

### 1.1	Scope

This specification document provides the requirements for the installation, programming and configuration of a complete Honeywell Farenhyt Series IFP-300ECS digital protocol analog addressable fire alarm system with integrated Emergency Communication System capabilities (ECS). This system shall include, but not be limited to, system cabinet, power supply, voice command module, microphone, built in Signaling Line Circuit (SLC), 160 character LCD annunciator, four programmable notification circuits, built in dual line, IP and optional cellular digital communicator associated peripheral devices, batteries, wiring, conduit and other relevant components and accessories required to furnish a complete and operational life safety system.

### 1.2	Work Included

#### 1.2.1	General Requirements

The contractor shall furnish and install a complete 24 VDC, electrically supervised, analog addressable fire alarm system with emergency communication as specified herein and indicated on the drawings. The system shall include but not be limited to all control panels, audio amplifiers, power supplies, initiating devices, audible and visual notification appliances, alarm devices, and all accessories required to provide a complete operating fire alarm, carbon monoxide alarm and emergency communication system.

#### 1.2.2	Listings

All fire alarm system equipment shall be listed for it’s intended purpose and be compatibility listed to assure the integrity of the complete system.

### 1.3	Standards

The fire alarm equipment and installation shall comply with the current provisions of the following standards and shall be listed for it’s intended purpose and be compatibility listed to insure integrity of the complete system.

#### National Electric Code, Article 760

#### National Fire Protection Association Standards:

NFPA 70		National Electrical Code

NFPA 72		National Fire Alarm and Signaling Code

NFPA 101 		Life Safety Code

NFPA 720		Standard for the Installation of CO Detection

#### Local and State Building Codes

BOCA, National Building Code, Mechanical Code, Fire Prevention Code

#### Local Authorities Having Jurisdiction

#### 1.3.5	Underwriters Laboratories Inc.

All equipment shall be approved by Underwriters Laboratories, Inc. for its intended purpose, listed as power limited by Underwriters Laboratories, Inc., for the following standards as applicable:

UL 864 UOJZ 	Control units for Fire Protective Signaling Systems

Local Signaling Unit

Central Station Signaling Protected Premises Unit

Remote Signaling Protected Premises Unit.

Water Deluge Releasing Unit

UL 2572	Mass Notification Standard

UL 2075	CO Detectors Connected to FACP

UL 268 	Smoke Detectors for Fire Protective Signaling systems

UL 268A 	Smoke Detectors for duct applications

UL 217		Smoke Detectors for Single Stations

UL 521 	Heat Detectors for Fire Protective Signaling systems

UL 228 	Door Holders for Fire Protective Signaling systems

UL 464 	Audible Signaling appliances

UL 1638 	Visual Signaling appliances

UL 38	 	Manually Activated Signaling Boxes

UL 346 	Waterflow indicators for Fire Protective Signaling systems

UL 1481 	Power Supplies for Fire Protective Signaling systems.

UL1711	Amplifiers for Fire Protection Signaling Systems

#### 1.3.6   Americans with Disabilities Act (ADA)

All visual Notification appliances and manual pull stations shall comply with the requirements of the Americans with Disabilities Act.

  - General Requirements

    - Manufacturers/Distributors Services

      - The following supervision shall be provided by a factory trained and certified service technician from the distributor of the fire alarm equipment. The technician shall be trained and shall have a minimum of two (2) years of service experience in the fire alarm industry. The technicians name shall appear on equipment submittals and a copy of his manufactures trained shall be sent to the project engineer. The technician shall be responsible for the following items:

- A pre installation visit to the job site to review equipment submittals and to verify the method by which the system is to be wired.

- During the installation the certified technician shall be on site or make periodic visits to verify installation and wiring of the system. He shall also supervise the completion of conduit rough, wires pulled into conduit and wiring rough, and ready for trim.

- Upon completion of wiring, final checkout and certification of the system shall be made under the supervision of this technician.

- At the time of the formal checkout, technician shall give operational instructions to the owner and or his representative on the system.

#### 1.4.2	Submittals

The contractor shall submit three (3) complete sets of documentation within thirty (30) calendar days after award of the purchase order.  Indicated in the document will be the type, size, rating, style, catalog number, manufacturer’s names, photos, and /or catalog data sheets for all items proposed to meet these specifications.  The proposed equipment shall be subject to the approval of the Architect/Engineer and no equipment shall be ordered or installed on the premises without that approval.

NOTE: DOCUMENTATION - Submittal of shop drawings shall contain at least three (3) copies of original manufacturer specification and installation instruction sheets. Subsequent information may be copies. All equipment and devices on the shop drawings to be furnished under this contract shall be clearly marked in the specification sheets.

Supplier qualifications shall be submitted indicating years in business, service policies, warranty definitions, NICET certification, and completion of factory training program and a list of similar installations.

Contractor qualifications shall be supplied indicating years in business and prior experience with installations that include the type of equipment that is to be supplied.

The contractor shall provide hourly service rates, performed by a factory trained technician for this installed life safety system with the submittal.  Proof of training and authorization shall be included with the submittal.  These hourly service rates shall be guaranteed for a 1-year period.

#### Contract Close-out Submittals

Deliver two (2) copies of the following to the owner’s representative within Thirty (30) days of system acceptance.  The closeout submittals shall include:

- Installation and Programming manuals for the installed life safety system.

- Point to point diagrams of the entire life safety system as installed.  This shall include all connected smoke detectors and addressable field modules.

- All drawings must reflect device address as verified in the presence of the engineer and/or end user.

#### Warranty

Unless otherwise specified, all materials, installation and workmanship shall have a warranty for a three (3) year period.  A copy of the manufacturer warranty shall be provided with the close out documentation.

#### 1.4.4	Products

This life safety system specification must be conformed to in its entirety to ensure that the installed and programmed life safety system will accommodate all of the requirements and operations required by the building owner.  Any specified item or operational feature not specifically addressed prior to the bid date will be required to be met without exception.

Submission of product purported to be equal to those specified herein will be considered as possible substitutes only when all of the following requirements have been met:

- Any deviation from the equipment, operations, methods, design or other criteria specified herein must be submitted in detail to the specifying architect or engineer a minimum of ten (10) working days prior to the scheduled submission of bids. Each deviation from the operation detailed in these specifications must be documented in detail, including page number and section number, which list the system function for which the substitution is being proposed.

- A complete list of such substituted products with three (3) copies of working drawings thereof shall be submitted to the approved Architect and/or Consulting Engineer not less than ten (10) working days prior to the scheduled submission of bids.

- The contractor or substitute bidder shall functionally demonstrate that the proposed substitute products are in fact equal in quality and performance to those specified herein.

#### General Equipment and Materials Requirements

All equipment furnished for this project shall be new and unused.  All components shall be designed for uninterrupted duty.  All equipment, materials, accessories, devices and other facilities covered by this specification or noted on the contract drawings and installation specification shall be best suited for the intended use and shall be provided by a single manufacturer.  If any of the equipment provided under this specification is provided by different manufacturers, then that equipment shall be “Listed” as to its compatibility by Underwriters Laboratories (UL), if such compatibility is required by UL standards.

#### 1.4.6	Satisfying the Entire Intent of these Specifications

It is the contractor’s responsibility to meet the entire intent of these specifications. Deviations from the specified items shall be at the risk of the contractor until the date of final acceptance by the architect, engineer and owner’s representative.  All costs for removal, relocation, or replacement of a substituted item shall be at the risk of the electrical contractor.

SECTION TWO: SPECIFICATIONS

### 2.1	General

#### 2.1.1	Control Panel with Emergency Communication System

The fire alarm control panel (FACP) shall be the Honeywell Farenhyt Series IFP-300ECS analog addressable fire alarm control panel with emergency communication system.  The audio amplifiers shall be the Silent Knight ECS-50W, ECS-125W, ECS-INT50W or ECS-DUAL50W units.  The FACP must have a 6 amp power supply and be capable of expansion to a minimum of 102 total amps via bus connected expander modules that supervise low battery, loss off AC and loss of communication.

The system must contain at least one (1) Honeywell Farenhyt Series ECS-50W, ECS-125W, ECS-INT50W or ECS-DUAL-50W amplifier and shall be expandable from 50 to 1000 watts utilizing up to 7 additional amplifiers.  The ECS-50W and ECS-125W amplifiers shall be capable of adding a 4 zone splitter (ECS-CE4) to distribute the audio information to different locations in the installation.  The system shall have the capability of controlling up to 40 notification zones.  The amplifiers must contain the capability of being remotely located through a four-wire SBUS communications circuit and a two-wire VBUS voice circuit.  The system shall have the capability of adding up to 7 ECS-LOCs local operating consoles.

The voice evacuation system must have the capability of downloading fifteen (15) 60 second messages and utilize DSP technology for higher audio intelligibility.

The voice evacuation system shall be capable of operating at 25vrms or 70.7vrms (ECS-50W, ECS-INT50W and ECS-DUAL50W only) and must be field selectable at the amplifier level.  Systems that require additional modules for voltage conversion shall not be accepted.

The FACP must have Day/Night sensitivity capabilities on detectors and be capable of supporting up to 254 analog addressable points. This shall be accomplished via signaling line circuits (SLC) capable of supporting a minimum of 127 devices of any mix and match.  The main panel will contain one SLC circuit with the option of utilizing 5815XL expander modules.  The communication protocol on the SLC loop must be digital.

The FACP must support a minimum of four programmable notification circuits.  The panel must have a built in 160 character LCD annunciator with the capability of having an additional supervised remote annunciators connected in the field.

The FACP must have a built in UL approved IP and digital communicator with the option of adding a cellular module for communications.  The communicator must allow local and remote up/downloading of system operating options, event history, and detector sensitivity data.

The FACP must automatically test the smoke detectors in compliance with NFPA standards to ensure that they are within listed sensitivity parameters and be listed with Underwriters Laboratories for this purpose.

The FACP must compensate for the accumulation of contaminants that affect detector sensitivity.  The FACP must have day/night sensitivity adjustments, maintenance alert feature (differentiated from trouble condition), detector sensitivity selection, auto-programming mode (Jumpstart) and the ability to upgrade the core programming software on site or over the telephone.

The main communication bus (SBUS RS485) shall be capable of class A or class B configuration with a total SBUS length of 6,000 feet.

The FACP shall have a Jumpstart feature that can automatically enroll all properly connected accessories into a functional system.

The FACP must have the ability to upgrade the firmware revision from a laptop where the FACP is installed.

Panels that do not have these capabilities will not be accepted.

#### 2.1.2	System Wiring

The Signaling Line Circuit (SLC) and Data Communication Bus (SBUS) shall be wired with standard NEC 760 compliant wiring.  No twisted, shielded or mid capacitance wiring is required for standard installations.  All FACP screw terminals shall be capable of accepting 14-18 AWG wire. All system wiring shall be in accordance with the requirements of NFPA 70, the National Electrical Code (NEC) and also comply with article 760 of the NEC.

2.1.3	Signaling Line Circuits

Each SLC shall be capable of a wiring distance of 10,000 feet from the panel or SLC driver module (5815XL) and be capable of supporting 127 devices.  The communication protocol to SLC devices must be digital.  Any SLC loop device, which goes into alarm, must interrupt the polling cycle for priority response from the FACP.  The FACP must respond consistently to a device that goes into alarm on an SLC within 10 seconds. The auxiliary 5815XL SLC loop module must be capable of being located up to 6,000 feet from the FACP on a SBUS, which is separate from the SLC. The SLC shall be capable of functioning in a class A or class B configuration.

#### 2.1.4	SLC Loop Devices

Devices supported must include analog photoelectric detectors, analog heat detectors, addressable input modules, relay output modules or addressable notification modules.  Each SLC loop shall support up to 127 devices of any mix and match.

#### 2.1.5	Analog Detector Functions

The products of combustion detectors must communicate analog values using a digital 		protocol to the control panel for the following functions:

- Automatic compliance with NFPA 72 standards for detector sensitivity testing

- Drift compensation to assure detector is operating correctly

- Maintenance alert when a detector nears the trouble condition

- Trouble alert when a detector is out of tolerance

#### 2.1.6	Sensitivity Function

The FACP shall have the ability to set three different sensitivity levels.  A zone can be programmed to a day and a night sensitivity value.  The day/night schedule shall allow for 16 holiday dates that are user programmable to allow the FACP to respond at the night level on those days.

#### 2.1.7	Programmable Notification Circuits

The FACP shall support four programmable notification circuits that are capable of being programmed as supervised reverse polarity notification circuits or supervised auxiliary power circuits that can be programmed as continuous, resettable or door holder power.  The circuits can be configured as four Class B outputs, two Class B and one Class A outputs or two Class A outputs.

    - Addressable Notification Module

The contractor shall furnish and install where indicated on the plans, addressable notification modules, Honeywell Model SD500-ANM.  The modules shall be U.L. listed compatible with Honeywell Farenhyt Series IFP-300ECS fire alarm control panel. The notification module must provide one class A (Style Z) or class B (Style Y) notification output with one auxiliary power input. The notification module must be suitable for mounting in a standard 4 square electrical box and must include a plastic cover plate. The notification module must provide an LED that is visible from the outside of the cover plate. The notification module must be fully programmable for such applications as required by the installation. The SD500-ANM shall reside on the SLC loop and can be placed up to 10,000 feet from the control or 5815XL SLC loop module.

#### 2.1.8	Annunciator

The main control must have a built in annunciator with a 160-character LCD display and feature LED’s for Alarm, Supervisory, Trouble, Silenced and Power.  When in the normal condition the LCD shall display time and date based on a 200 year clock which is capable of automatic daylight savings time adjustments.  All controls and programming keys are silicone mechanical type with tactile and audible feedback.  Keys have a travel of .040 in.  No membrane style buttons will be permissible. The annunciator must be able to silence and reset alarms.  The annunciators must have twenty levels of user codes that will allow the limitation of operating system programming to authorized individuals.

#### 2.1.9	Remote Annunciators

The fire system shall be capable of supporting remote annunciators.  LCD Remote annunciator, Model RA-2000, shall have the same control and display layout so that they match identically the built in annunciator. Remote annunciators shall be available in two colors, red and light gray. Remote annunciators shall have the same functionality and operation as the built-in annunciator. All annunciators must have 160-character LCD displays and must feature five LED’s for Alarm, Supervisory, Trouble, Silenced, and Power. All controls and programming keys are silicone mechanical type with tactical and audible feedback. Keys shall have a travel of .040 inches. No membrane style buttons will be permitted.

The annunciator must be able to silence and reset alarms. The annunciator must have twenty levels of user codes that will limit the operating system programming to authorized individuals. The control panel must allow all annunciators to accommodate multiple users input simultaneously. Remote annunciators shall be capable of operating at a distance of 6,000 feet from the main control panel on unshielded, non-twisted cable.

2.1.10 	I/O Module

The fire system shall be able to support I/O modules (SK5880) that shall be used to drive remote LED graphic style displays and accommodate up to eight dry contact type switch inputs, including ECS inputs.  The I/O modules shall each drive up to 40 LEDs without requiring external power connections.  The I/O module inputs shall be supervised and be suitable for alarm and trouble circuits as well as reset and silence switches.

#### 2.1.11	Serial/Parallel Interface

The fire system shall be capable of supporting up to two serial/parallel interfaces (SK5824) that are capable of driving standard computer style printers.  The interface shall be programmable for the serial and parallel ports and allow printing of events as they occur.

#### 2.1.12	Distributed Power Modules

The contractor shall supply power modules, Models RPS-1000 and 5496, compatible with the IFP-300ECS fire alarm control panel. The RPS-1000 power module must have 6 amps of output power, six Flexput™ circuits rated at 3amps each, and two form C relay circuits rated at 2.5 amps at 24 volts DC. The six Flexput™ circuits shall be capable of being programmed as supervised reverse polarity notification circuits or supervised auxiliary power circuits that can be programmed as continuous, resettable or door holder power.  The circuits shall also be programmable as input circuits in class A or B configurations to support dry contact or compatible two wire smoke detectors.

The RPS-1000 shall be capable of being connected via an RS-485 system bus (SBUS) at a maximum distance of 6,000 feet from the main control panel. The RPS-1000 shall contain an additional RS-485 bus that is completely compatible with all IFP-300ECS add on modules; including 5815XL SLC expanders, RA-2000-SK5865-SK5880 annunciators, 5824 serial/parallel module and addressable devices. The RPS-1000 will also act as a bus repeater so that additional RS-485 (modules) devices can be connected at a maximum distance of 6,000 feet from the power module.

The 5496 power module must have 6 amps of output power and four circuits rated at 3 amps each.  The four circuits can be programmed as notification outputs or auxiliary power outputs of door holder, constant, sounder base synchronization and resettable types.

#### 2.1.13	Digital Communicator

The digital/IP communicator must be an integral part of the control panel and be capable of reporting all zones or points of alarm, supervisory, and trouble as well as all system status information such as loss of AC, low battery, ground fault, loss of supervision to any remote devices with individual and distinct messages to a central station or remote station.  The communicator must also be capable of up/downloading of all system programming options, event history and detector sensitivity compliance information to a PC on site or at a remote location.

The communicator shall transmit the information by one or more of the following means of communication – internet, cellular or standard telephone lines.  The communicator must be capable of reporting via SIA and Contact ID formats.  The communicator shall have a delayed AC loss report function which will provide a programmable report delay plus a 10-25 min random component to help ease traffic to the central station during a power outage. No controls that use external modems for remote programming and diagnostics shall be accepted.

#### 2.1.14	Dry Contacts

The FACP will have three form “C” dry contacts, one will be dedicated to trouble conditions, the other two will be programmable for alarm, trouble, sprinkler supervisory, notification, pre-alarm, waterflow, manual pull, aux. 1 or aux. 2.  The trouble contact shall be normal in an electrically energized state so that any total power loss (AC and battery) will cause a trouble condition.  In the event that the microprocessor on the FACP fails the trouble contacts shall also indicate a trouble condition.

#### 2.1.15	Ground Fault Detection

A ground fault detection circuit shall be used to detect positive and negative grounds on all field wiring. The ground fault detector shall operate the general trouble devices as specified but shall not cause an alarm to be sounded. Ground faults will not interfere with normal operation, such as alarm, or other trouble conditions.

#### 2.1.16	Overcurrent Protection

All low voltage circuits will be protected by microprocessor controlled power limiting or have a self restoring polyswitches for the following: smoke detector power, main power supply, indicating appliance circuits, battery standby power and auxiliary output.

#### 2.1.17	Test Functions

A “Lamp Test” mode shall be a standard feature of the fire alarm control panel and shall test all LED’s and the LCD display on the main panel and remote annunciators.

A “Walk Test” mode shall be a standard feature of the fire alarm control panel. The walk test feature shall function so that each alarm input tested will operate the associated notification appliance for 6 to 180 seconds.  The FACP will then automatically perform a reset 	and confirm normal device operation.  The event memory shall contain the information on the point tested, the zone tripped, the zone restore and the individual points return to normal.

A “Fire Drill” mode shall allow the manual testing of the fire alarm system notification circuits.  The fire drill shall be capable of being controlled at the main annunciator, remote annunciators and via a remote contact input.

A “Bypass Mode” shall allow for any point or NAC circuit to be bypassed without effecting the operation of the total fire system.

#### 2.1.18	Remote Input Capabilities

The control panel shall have provisions for supervised switch inputs for the purpose of alarm reset and alarm and trouble silence.

#### 2.1.19	Notification Appliance Mapping Structure

All notification circuits and modules shall be programmable via a mapping structure that allows for a maximum of 999 output groups.  Each of these groups shall have the ability to be triggered by any of the panels 999 zones, panel wide events, or site wide events.  Additionally each zone, panel, or site will individually control the cadence pattern of each of the groups that it is mapped to so that devices can indicate a variety of conditions.  The zone, panel, or site shall be capable of issuing a different cadence pattern for each of the groups under its control.  The mapping structure must also allow a group to be designated to “ignore cadence” for use with strobes and other continuous input devices.  Zones shall have ten different output categories; Detector Alarm, Trouble, Supervisory, Pre-alarm, Waterflow, Manual Pull, Zone Auxiliary 1 and Zone Auxiliary 2, CO Alarm and CO

Supervisory.  

Each of the categories shall have the ability to control output groups with a cadence pattern.  The patterns are; March code, ANSI 3.41, Single Stroke Bell Temporal, California Code, Zone 1 Coded, Zone 2 Coded, Zone 3 Coded, Zone 4 Coded, Zone 5 Coded, Zone 6 Coded, Zone 7 Coded, Zone 8 Coded, Custom Output Pattern 1, Custom Output Pattern 2, Custom Output Pattern 3, Custom Output Pattern 4, Constant, System Sensor Synchronization, Wheelock Synchronization, Gentex Synchronization, Amseco Synchronization, and Faraday Synchronization.  This mapping/cadence pattern shall be supported by all system power supplies.  15 recordable one minute messages are available that can be mapped to eight ECS buttons.   ECS messages can have priority

over fire alarm outputs.

#### 2.1.20	On-board Programmer

The FACP shall have an on board programmer which will allow for all system functions and options, except for mapping, to be programmed via the on board annunciator keypad.  Any panel that does not have this capability will not be accepted.

#### 2.1.21	Downloading Software

The fire alarm control panel must support up/downloading of system programming from a PC.  The FACP must also be able to download the detector sensitivity test results and a 1,000 event system event buffer to the PC.  Communication shall take place over a direct connection to the PC and/or via the same communication method as the built in digital communicator and shall not require an external modem to be connected to the panel.  The downloading software shall contain a code that will block unauthorized persons from accessing the panel via direct connection or over the phone lines.

#### 2.1.22	English Language Descriptions

The FACP shall provide the ability to have a text description of each system device, input zone and output group on the system.  The use of individual lights to provide descriptions will not be acceptable.

### 2.2	SYSTEM OPERATION

#### 2.2.1	Alarm

When a device indicates any alarm condition the control panel must respond within 10 seconds.  All programmed audio and visual devices will activate at this time.  The Alarm or Supervisory LED on the annunciator(s) should light and the LCD should prompt the user as to the number of current events.  The alarm information must be stored in event memory for later review.  Event memory must be available at the main and all remote annunciators.

When the alarmed device is restored to normal, the control panel shall be required to be manually reset to clear the alarm condition, except that the alarms may be silenced as programmed.

An alarm shall be silenced at the main or remote annunciators.  When silenced, this shall not prevent the resounding of subsequent events if another event should occur (subsequent alarm feature).  When alarms are silenced the silenced LED on the control panel, and on any remote annunciators shall remain lit, until the alarmed device is returned to normal.

#### 2.2.2	Troubles

When a device indicates a trouble condition, the control panel System Trouble LED should light and the LCD should prompt the user as to the number of current events.  The trouble information must be stored in event memory for later review.  Event memory must be available at the main and all remote annunciators.

When the device in trouble is restored to normal, the control panel shall be automatically reset. The trouble restore information must be stored in event memory for later review.  Event memory must be available at the main and all remote annunciators.  A trouble shall be silenced at the main or remote annunciators.  When silenced, this shall not prevent the resounding of subsequent events if another event should occur.

#### 2.2.3	Supervision Methods

Each SLC loop shall be electrically supervised for opens and ground faults in the circuit wiring, and shall be so arranged that a fault condition on any loop will not cause an alarm to sound.  Additionally, every addressable device connected to the SLC will be supervised and individually identified if in a fault condition.  The occurrence of any fault will light a Trouble LED and sound the system trouble sounder, but will not interfere with the proper operation of any circuit which does not have a fault condition.

Each indicating appliance circuit shall be electrically supervised for opens, grounds and short circuit faults, on the circuit wiring, and shall be so arranged that a fault condition on any indicating appliance circuit or group of circuits will not cause an alarm to sound. The occurrence of any fault will light the trouble LED and sound the system trouble sounder, but will not interfere with the proper operation of any circuit which does not have a fault condition.

## SECTION THREE: SYSTEM COMPONENTS

### 3.0	CONTROL UNIT

#### 3.1	System Cabinet

##### 3.1.1	Mounting

The system cabinets shall be black and can be either surface or flush mounted.

##### 3.1.2	Audible System Trouble Sounder

An audible system trouble sounder shall be an integral part of the control unit. Provisions shall also be provided for an optional supervised remote trouble signal.

#### 3.2	Power Supply and Charger

The entire system shall operate on 24 VDC, filtered switch mode power supply with the 		rated current available of 6 Amps. The FACP must have a battery charging circuit 		capable of complying with the following requirements:

Sixty (60) hours of battery standby with five (5) minutes of alarm signaling at the 	end of this sixty (60) hour period (as required per NFPA 72 remote station signaling requirements) using rechargeable batteries with automatic charger to maintain standby gel-cell batteries in a fully charged condition.

OR

Twenty-four (24) hours of battery standby with five (5) minutes of alarm signaling at the end of this twenty-four (24) hour period (as required per NFPA 72 central station signaling requirements) using rechargeable batteries with automatic charger to maintain gel-cell batteries in a fully charged condition.

The power supply shall comply with U.L. Standard 864 for power limiting.

The FACP will indicate a trouble condition if there is a loss of AC power or if the batteries are missing or of insufficient capacity to support proper system operation in the event of AC failure.  A “Battery Test” will be performed automatically every minute to check the integrity of the batteries.  The test must disconnect the batteries from the charging circuit and place a load on the battery to verify the battery condition.

In the event that it is necessary to provide additional power one or more of the Model RPS-1000 or 5496 distributed power modules shall be used to accomplish this purpose.

##### 3.2.1	Connections and Circuits

Connections to the light and power service shall be on a dedicated branch circuit in accordance with the National Fire Alarm Code NFPA 72, National Electrical Code (NEC) NFPA 70, and the local authority having jurisdiction (AHJ).  The circuit and connections shall be mechanically protected.

A circuit disconnecting means shall be accessible only to authorized personnel and shall be clearly marked “FIRE ALARM CIRCUIT CONTROL”.

SECTION FOUR:  ACCESSORY COMPONENTS

### 4.1	The FACP shall support the following devices on the RS-485 data bus:

ECS-NVCM	      Network Voice Control Module

ECS-SW24	      Additional 24 Zone Switch Module

ECS-50W	      50 Watt Amplifier

ECS-125W	      125 Watt Amplifier

ECS-DUAL50W    50/100 Watt Dual Channel Amplifier with 50 Watt Backup

ECS-INT50W	      50 Watt Internal Amplifier

ECS-CE4	      4 Zone Splitter

ECS-LOC	      Local Operator Console (15 max.)

5815XL	      Signaling Line Circuit Expander (SLC) Module

5824		      Printer Interface Module

RA-2000 	      LCD Remote Annunciator

5865-3	      LED Remote Annunciator

5865-4	      LED Remote Annunciator with reset and silence switches

5880 	      LED I/O module

RPS-1000	      Intelligent Distributed Power Module

5496		      Intelligent Distributed Power Module

### 4.2	The FACP shall support the operation of 127 devices per SLC loop without regard to type.

### The following devices shall be supported:

SD505-APS 		Addressable Photoelectric Smoke Detector

SD505-PHOTO	Addressable Photoelectric Smoke Detector

SD505-HEAT		Addressable Heat Sensor

SD505-6AB		6” detector base

SD505-DUCT		Addressable Duct Detector

SD505-DUCTR	Addressable Duct Detector with Relay

SD500-ARM		Addressable Relay Module

SD500-AIM		Addressable Input Module

SD500-MIM		Mini Input Module

SD500-ANM		Addressable Notification Module

SD500-SDM		Two Wire Smoke Detector Module

SD500-LIM		Isolation Module

SD505-6IB		Addressable Isolator base

SD505-6RB		Detector Relay Base

SD505-6SB		Detector Sounder Base

SD505-DTS-K		Remote Test Switch for Duct Detector

SD500-PS		Addressable Single Action Pull Station

SD500-PSDA		Addressable Dual Action Pull Station

The FACP shall support these other Silent Knight devices via addressable input, addressable notification, or addressable output modules.

PS-DALOB         	Dual Action Manual Pull Outdoor Listed

PS-DAH                	Dual Action Manual Pull Hex Key reset

PS-SATK		Single Action Manual Pull Station – Key Reset

PS-DATK		Dual action Manual Pull Station – Key Reset

PS-DASP		Dual action Manual Pull Station “Spanish”- Key reset

SB-I/O 		Surface mount back box for outdoor use.

  - Furnish and install, where shown on the drawings, the following devices

    - Manual Fire Alarm Stations

Manual fire alarm stations shall be non-coded, break glass, single or double action type, with a key operated test-reset lock in order that they may be tested, and so designed that after actual emergency operation, they cannot be restored to normal except by use of a key. The reset key shall be so designed that it will reset manual station and open FACP without use of another key.  An operated station shall automatically condition itself so as to be visually detected, as operated, at a minimum distance of fifty feet, front or side.  Manual stations shall be constructed of die cast metal or polycarbonate with clearly visible operating instructions on the front of the stations in raised letters.  Stations shall be suitable for surface mounting on matching backbox, or semi-flush mounting on a standard single-gang box, and shall be installed within the limits defined by the Americans with Disabilities Act (ADA) dependent on manual station accessibility or per local requirements. Manual stations shall be installed in conjunction with an addressable input module, SD500-AIM or SD500-MIM. Manual stations shall be Honeywell Underwriters Laboratories listed.

    - Remote Power Supplies

The remote power supplies for notification appliances shall be the Honeywell Model RPS-1000 or 5496. The Model RPS-1000 intelligent power supply shall wire on the main SBUS and be programmed through the IFP-300ECS. It will support 6 amps of 24 volt DC power with six programmable Flexput™ circuits, rated at 3 amps each. Two additional 5815XL SLC loop expanders shall be capable of be install in the cabinet. The power supply will also regenerate the SBUS for an additional 6000 feet of SBUS capability.

The Silent Knight 5496 intelligent power supply shall wire on the main SBUS and be programmed through the IFP-2000ECS.  It will support 6 amps of 24 volt DC power with 4 notification circuits, rated at 3 amps each.

The remote power supply model 5499 or 5495 may also be used on the system. These power supplies are activated by a notification circuit or an IDP-Control module and support 6 or 9 amps of 24VDC power, with 4 notification circuits, rated at 3amps each.

  - Notification Devices

The visible and audible/visible signal shall be System Sensor series signal devices and be listed by Underwriters Laboritories Inc. per UL 1971 and/or 1638 and UL 464.  The notification appliance (combination audible/visible units only) shall produce a peak sound output of 90dba or greater as measured in an anechoic chamber. The signaling appliance shall also have the capability to silence the audible signal while leaving the visible signal energized with the use of a single par of wires.  Additionally, the user shall be able to select either continuous or temporal tone output with the temporal signal having the ability to be synchronized.  The visible signaling appliance shall maintain a minimum flash rate of 1Hz or greater regardless or power input voltage. The appliance shall also be capable of meeting the candela requirements of the blueprints presented by the engineer and ADA. The appliance shall be polarized to allow for electrical supervision of the system wiring. The unit shall be provided with terminals with barriers for input/output wiring and be able to mount to a single gang or double gang box or double workbox with the use of an adapter plate. The unit shall have an input voltage range of 20-30 volts with either direct current or full wave rectified power.

4.5	Smoke Detectors

Smoke detectors shall be Silent Knight Model SD505-PHOTO ceiling mounted, analog/addressable photoelectric smoke detectors. The combination detector head and twist lock base shall be U.L. listed compatible with the Silent Knight IFP-2000ECS fire alarm control panel.  The base shall permit direct interchange with Silent Knight’s SD505-PHOTO or SD505-HEAT detectors. The base shall be the appropriate twist lock base SD505-6AB.  The smoke detector shall have a flashing status LED for visual supervision. When the detector is actuated, the flashing LED will latch on steady at full brilliance. The detector may be reset by actuating the control panel’s reset switch. The sensitivity of the detector shall be capable of being selected and measured by the control panel without the need for external test equipment.  The vandal security-locking feature shall be used in those areas as indicated on the drawing. The locking feature shall be field selectable when required. It shall be possible to perform a sensitivity test of the detector without the need of generating smoke. The test method shall simulate the effects of products of combustion in the chamber to ensure testing of the detector circuits.  Detectors shall have completely closed back to restrict entry of dust and air turbulence and have a 30 mesh insect screen. Electronics of the unit shall be shielded to protect against false alarms from E.M.I. and R.F.I.

  - Heat Detectors

Furnish and install analog/addressable heat detectors, Silent Knight model SD505-HEAT. The combination heat detector and twist lock base shall be U.L. listed compatible with the Silent Knight IFP-2000ECS fire alarm control panel.  The base shall permit direct interchange with the Silent Knight SD505-PHOTO or SD505-HEAT detectors. The base shall be appropriate twist lock base SD505-6AB.  The heat detector shall have a flashing status LED for visual supervision. When the detector is actuated, the flashing LED will latch on steady at full brilliance. The detector may be reset by actuating the control panel’s reset switch. The vandal security-locking feature shall be used in those areas as indicated on the drawings. Electronics of the unit shall be shielded to protect against false alarms from E.M.I. and R.F.I.

  - Duct Detectors

Duct Detector shall be Silent Knight Model SD505-DUCT or SD505-DUCTR.  The duct detector comes with a SD505-APS photoelectric smoke detector head.  The SD505-DUCTR comes with a built-in relay.

SECTION FIVE: WIRING

### 5.1	Installer’s Responsibilities

The installer shall coordinate the installation of the fire alarm equipment.  All conductors and wiring shall be installed according to the manufacturer’s recommendations.

It shall be the installer’s responsibility to coordinate with the supplier, regarding the 		correct wiring procedures before installing any conduits or conductors.

#### 5.2	Installation of System Components

System components shall be installed in accordance with the latest revisions of the 		appropriate NFPA pamphlets, the requirements contained herein, National Electrical 		Code, local and state regulations, the requirements of the fire department and other 		applicable authorities having jurisdiction (AHJ).

All wire used on the fire alarm system shall be U.L. Listed as fire alarm protection 		signaling circuit cable per National Electrical Code, Articles 760.

SECTION SIX: WARRANTY AND FINAL TEST

### 6.1	General

The contractor shall warrant all equipment and wiring free from inherent mechanical and electrical defects for one year (365 days) from the date of final acceptance.

#### 6.2	Final Test

Before the installation shall be considered completed and acceptable by the awarding 		authority, a test of the system shall be performed as follows:

- The contractor’s job foreman, a representative of the owner, and the fire department shall operate every building fire alarm device to ensure proper operation and correct annunciation at the control panel.

- At least one half of all tests shall be performed on battery standby power.

- Where application of heat would destroy any detector, it may be manually activated.

- The communication loops and the indicating appliance circuits shall be opened in at least two (2) locations per circuit to check for the presence of correct supervision circuitry.

When the testing has been completed to the satisfaction of both the contractor’s job foreman and owner, a notarized letter cosigned by each attesting to the satisfactory completion of said testing shall be forwarded to the owner and the fire department.

The contractor shall leave the fire alarm system in proper working order, and, without additional expense to the owner, shall replace any defective materials or equipment provided by him under this contract within one year (365 days) from the date of final acceptance by the awarding authority.

Prior to final test the fire department must be notified in accordance with local requirements.

### 6.3	As Built Drawings, Testing, and Maintenance Instructions

#### 6.3.1	As Built Drawings

A complete set of reproducible “as-built” drawings showing installed wiring, color coding, and wire tag notations for exact locations of all installed equipment, specific interconnections between all equipment, and internal wiring of the equipment shall be delivered to the owner upon completion of system.

##### 6.3.2	Operating and Instruction Manuals

Operating and instruction manuals shall be submitted prior to testing of the system. Three (3) complete sets of operating and instruction manuals shall be delivered to the owner upon completion.  User operating instructions shall be provided prominently displayed on a separate sheet located next to the control unit in accordance with U.L. Standard 864.